| Тема | Задатак | 2011 | Тип публ. | Број публ. | Извршиоци | Носилац |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 1. Истраживање метода брзог израчунавања амплитуда и фаза хармоника на потрошачу | х |  |  | М. Димитријевић, Д. Стевановић | В. Литовски, П. Петковић |
|  | 2. Истраживање метода и алгоритама за дефинисање активне, реактивне и снаге изобличења у условима нелинеарних изобличења и њиховог брзог израчунавања | х |  |  | Д. Стевановић, М. Димитријевић | В. Литовски, П. Петковић |
|  | 3. Истраживање метода дефиниције и израчунавања фактора снаге изобличења | х |  |  | Д. Стевановић М. Димитријевић | В. Литовски, П. Петковић |
|  | 4. Дефиниције хардверских решења имплементације алгоритама израчунавања хармоника, активне снаге, реактивне снаге, снаге изобличења и фактора снаге изобличења. | х | М61, М51 | 2 | Д. Стевановић М. Димитријевић | В. Литовски, П. Петковић |

# Exploring methods for fast harmonic magnitude and phase calculation

### Sinusoidal Voltage and Current in Single Phase Circuits

A sinusoidal voltage source

supplying a linear load, will produce a sinusoidal current

where VRMS is the RMS value of the voltage, IRMS is the RMS value of the current, ω is the angular frequency, φ is the phase angle and t is the time. The instantaneous power is

and can be represented as

Using appropriate transformations we can write:

and

where

represent real (P) and reactive (Q) power.

It can be easily shown that the real power presents the average of the instantaneous power over a cycle:

where t0 is arbitrary time (constant) after equilibrium, and T0 is the period (20 ms in European and 1/60 s in American system, respectively).

The reactive power Q is the amplitude of the oscillating instantaneous power pq. The apparent power is the product of the root mean square value of current times the root mean square value of voltage:

or:

Power factor is simply defined as the ratio of real power to apparent power:

For pure sinusoidal case, using equations (7), (10) and (11) we can calculate:

### Sinusoidal Voltage and Current in Polyphase Circuits

The power concepts developed for single-phase circuits with sinusoidal voltages and currents can be extended to polyphase circuits. Equations  can be rewritten to define power terms equivalent to the single-phase terms. In these equations, n represents a phase number, N is the total number of phases, and φn phase difference:

The apparent power is defined by equation .

Power factor is defined by equation . Note that the power factor is not always equal to the cosine of the phase angle. In many three-phase balanced systems, the phase angles of all three phases are equal and the cosine relationship holds. In unbalanced systems, each phase has a different phase angle, the phase voltages and currents are not equal, and the cosine relationship is no longer valid.

### Nonlinear Loads in Single Phase Circuits

In the presence of nonlinear loads the system no longer operates in sinusoidal condition and use of fundamental frequency analysis does not apply any more. Traditional power system quantities such as effective value, power (active, reactive, apparent), and power factor need to be numerically calculated from sampled voltage and current sequences by performing the FFT algorithm.

The RMS value of some periodic physical entity X (voltage or current) is calculated according to the well-known formula:

where x(t) represents time evolution, T is the period and t0 is arbitrary time. For any periodic physical quantity x(t), we can produce a Fourier representation:

or

whererepresents DC component,  the magnitude of kth harmonic,  the phase of the  kth harmonic, and the angular frequency.

The Fourier coefficients ak, bk are calculated as:

and

The RMS value of the kth harmonic is

We can calculate total RMS value as

where M is highest order harmonic taken into calculation. Index “1” denotes first or fundamental harmonic, and index “H” denotes contributions of higher harmonics.

Equations  –  need to be rewritten for voltage and current. Practically, we operate with sampled values and integrals  and  are transformed into truncated series.

For a single-phase system where k is the harmonic number, φk phase difference between voltage and current of kth harmonic, and M is the highest harmonic, the total active power is given by:

The first addend in the sum , denoted with P1, is the fundamental active power. The rest of the sum, denoted with PH, is harmonic active power.

The total reactive power is given by:

It should be noted that the actual contribution of harmonic frequencies to active and reactive power is small (usually less than 3% of the total active or reactive power). The major contribution of higher harmonic to the power comes as distortion power D:

The apparent power is given by formula  and it can be written:

where S1 represents the fundamental apparent power, DV the voltage distortion power, DI the current distortion power and SH the harmonic apparent power. S1 and SH are

where DH represents harmonic the distortion power. The total apparent power is

It is obvious that for sinusoidal voltages and currents,  reduces to .

The total harmonic distortions, THD, are calculated from the following formulas:

and

where Ij,Vk j,k=1, 2, …, M stand for the harmonic of the current or voltage. It can be shown that:

The fundamental power factor or displacement power factor is given by the following formula:

The total power factor DPF, defined by equation , taking into account  and , becomes

and substituting  and :

In real circuits, PH<<P1 and voltage is almost sinusoidal (THDV<5%), leading to a simpler expression for TPF:

### Nonlinear Loads in Polyphase Circuits

For polyphase systems, active, reactive and distortion powers are defined for each phase and total powers are sum of all phase powers:

Voltages Vn,k,RMS are phase-to-neutral voltages. Indexes n and k denotes phase number and harmonic order, respectively. N is number of phases and M is number of harmonics taken into calculation.

The apparent power can be defined as sum of apparent powers per phase – arithmetic apparent power (SA) or as vector apparent power (S):

Note that Vn,RMS and In,RMS are total RMS values per phase, and n is a phase index.

SA uses arithmetic addition of vector magnitudes and is equal to apparent power S only if the polyphase voltages and currents have equal magnitudes and equal phase difference; a situation that often exists in balanced three-phase systems. The two alternative definitions of apparent power, S and SA, give rise to two possible values for power factor, calculated using equation .

### Acquisition and discrete Fourier transform

Signal acquisition can be mathematically represented by sum of convolution of continual function  in time domain and Dirac delta function:

where TS represents sampling period, Dirac delta function defined as of the sequence of Gaussians

is continual function with non-zero values in discrete time points nTS. The frequency of sampling  must fulfill Nyquist–Shannon criterion,  where B represents signal bandwidth. If  is periodical signal, with period T0 – which is also period of elementary harmonic – bandwidth is , where M represents order of the highest harmonic taken into account.

Discrete Fourier transform maps time domain function into frequency domain, can be derived from continual transform equation:

where f is frequency, ,  is time domain function and  frequency domain representation. Discrete Fourier transform (DFT) maps discrete values of  into discrete spectrum Xk:

where k=0,1,…,N-1 is index of discretized spectrum, n sample index and N total number of samples calculated into DFT. The calculated spectrum is made of individual components at the frequency bins which are expressed as:

where Δf denotes frequency bin quantum. Exact DFT is possible if two conditions are fulfilled:

- signal  is periodic, period is T0,

- the observation time NTs is integer multiple of period T0 corresponding to signal .

DFT implementation defined by equation  requires N2 complex number calculations. Optimized FFT algorithm requires as small as  operations.

Main disadvantage of DFT is failing to accomplish the second condition in practice: if frequency of  varies, observation time will not be integer multiple of the period. In this case, the result of DFT differs from expected result. The difference is characterized by wider signal spectrum and an amplitude error. In order to eliminate this disadvantage, one can implement other algorithms, such as Goertzel algorithm or Adaptive Real Time Monitoring (ARTM) algorithm [1], or utilize iterative methods for harmonic amplitude and phase calculations, like Newton method [2,3] or STLS algorithm [4].

Fourier transform  maps real, or complex number sequence into complex sequence. Inherent property of transform is

If sequence  is real, values Xk i X-k are complex-conjugate:

RMS value and phase for kth harmonic are:

## Reference

Petre Minciunesc, Gabriel Antonesei, “Novel harmonic analysis method for smart metering,” EE Times Europe, 2011

Vladimir V. Terzija, Vladimir Stanojević, Marjan Popov, Lou van der Sluis, “Digital Metering of Power Components According to IEEE Standard 1459-2000 Using the Newton-Type Algorithm,” IEEE Transactions on Instrumentation and Measurement, Vol. 56, No. 6, December 2007, pp. 2717-2724

Vladimir V. Terzija, Vladimir Stanojević, “Two-Stage Improved Recursive Newton-Type Algorithm for Power-Quality Indices Estimation,” IEEE Transactions on Power Delivery, Vol. 22, No. 3, July 2007, pp. 1351-1359

Vladimir V. Terzija, Vladimir Stanojević, “STLS Algorithm for Power-Quality Indices Estimation,” IEEE Transactions on Power Delivery, Vol. 23, No. 2, April 2008, pp. 544-552

## Published papers

1.1 (Task 1.1) (category M63) Dimitrijević, M., Jovanović, B.: „Određivanje THD faktora bazirano na integrisanim kolima Teradian 71M6533 i IMPEG“,  Zbornik LV konferencije ETRAN, Banja Vrućica, Bosna i Hercegovina, 06.06.-09.06., 2011, EL 3.4, ISBN 978-86-80509-66-2

1.2 (Task 1.1) (category M23) Dimitrijević, M., Litovski, V.: „Power Factor and Distortion Measuring for Small Loads Using USB Acquisition Module“, Journal of Circuits Systems and Computers, World Scientific Publishing Co. Pte. Ltd., Singapore, DOI 10.1142/S0218126611007657, August, 2011, Vol. 20, No. 5, pp. 867-880, ISSN 0218-1266

1.3 (Task 1.1) (category M63) Dimitrijević, M., Litovski, V.: „Virtual Instrument for Three-Phase Power Quality Analysis,“ VIII Simposium on Industrial Electronics INDEL 2010, Banja Luka, Bosnia and Herzegovina, 04.11.-06.11., 2010, pp. 189-194, ISBN 978-99955-46-03-8

1.4 (Task 1.1) (category M33) Dimitrijević, M., Litovski, V.: „Computer Based Power Factor and Distortion Measuring for Small Loads,“  Proceedings of the Small Systems Simulation Symposium 2010, Niš, 12.02.-14.02., 2010, pp. 81-85, ISBN 987-86-6125-006-4